## Slide 1
Notes: talking about vulnerabilities me and my teammate Patrick DeSantis discovered in the MicroLogix 1400 Programmable Logic Controller and how they can be chained together to gain full control over the firmware on the device
font: https://www.google.com/fonts#UsePlace:use/Collection:Exo+2

## Slide 2: INTRODUCTION
Notes: Jared
Talos
Focus Primarily Embedded systems research and detection
Search for vulnerabilities in devices
Work to create coverage based on those vulns as well as others from intel sources for Snort to detect and alert

## Slide 3: PROJECT ORIGIN
Notes: !!!!! USE NOTES HERE
Advanced Persistent Thirst
    Remote controlled kegerator
    Uses ICS equipment that could be found in the field
    MicroLogix 1400 selection rationale
      Compact
      All in one device
      Commonly known PLC
  From Box to Backdoor
    First talk on the results of research into the devices used in APT
      Including the MicroLogix 1400
    Discussed vulns discovered during the process
      Namely a major SNMP issue

## Slide 4: PRIOR WORK
Thiago Alves
University of Alabama
Mark Gondree, Francisco Tacliad, and Thuy Nguyen
Sonoma State University & Naval Postgraduate School
Patrick DeSantis
Cisco Talos
Matthew Luallen
Cybati
Eyal Udassin
C4 Security
Ruben Santamarta and K. Reid Wightman
Digitalbond
Notes: Time: 30 Seconds
Notes:
  Numerous other people have worked on related equipment
  Interesting work that helped while working on the project

## Slide 5: PROJECT GOALS
Remotely Control the Device
Modify Configuration to Gain Additional Access
Flash the Device with Modified Firmware
Notes: Time: 1minute
Notes:
  Determine a way to interact with the device without being physically connected
  Change the settings applied by engineers to get the device into a desired state
  Reflash the PLC with our own firmware to achieve the desired end goal

## Slide 6: PROGRAMMABLE LOGIC CONTROLLER (PLC)
Notes: Est Time Marker: 4 Minutes
!!!!!!!!! Use notes
Computer
Fancy casing
Designed to operate in sub-optimal conditions
  Out in the weather
  In a factory
  Etc
Used to automate the control of a device or system according to a defined program
  Could be as simple as turning on a light at night
  Could be as complex as controlling the precise amounts of different elements being combined together
Uses a special operating system designed to keep the device’s input and output controls as close to real time as possible

## Slide 7: PLC - MICROLOGIX 1400
Typical applications for our MicroLogix™ programmable controllers include:
  Material Handling
  Packaging Applications
  General Industrial Machinery
  Printing
  Food and Beverage
  Pharmaceutical
  Water Wastewater / SCADA
  Clutch/Brake control
  Position Control - Pick-and-place / Conveyo
- Allen Bradley
Notes: Time: 2 minutes
Notes:
  Micrologix Line
    Location
      Reference on screen
    Uses
      Smaller environments
      Hence ‘micro’
    Notable elements in the 1400
      Included I/O
      On-device LCD screen
Applications Reference:
https://ab.rockwellautomation.com/Programmable-Controllers/MicroLogix-1400#applications

## Slide 8: PLC – KEYSWITCH STATES
RUN
REMOTE
PROG
Notes: Time: 2minutes
Notes:
  Keyswitch
    Changes the operating mode of the CPU
  PROG
    Programming mode
    Non-executing mode
    Allows for reprogramming of the device
  RUN
    Execution Mode
    Non-Programming mode
    Program is running in this mode
  REMOTE
    A melding of PROG and RUN
    Contains a programming mode
    Contains a run mode
    Contains others as well
    Sub Modes
      REMOTE RUN
      REMOTE PROG
      Others not relevant to this talk

## Slide 9: PLC - COMMUNICATION PROTOCOLS
Programmable Controller Communication Commands
(PCCC)
Ethernet
IP
TCP
EtherNet/IP
PCCC
Notes: Time: 30s
Notes:
  Discuss PCCC and where it fits into the encapsulation structure
  Emphasize that it EtherNet/IP is its own protocol, not just referencing L2&3

## Slide 10: PLC - PCCC STRUCTURE
PCCC
CMD
Data
FNC
TNS
Notes: Time: 30s
Notes:
  Basic format of a PCCC message
  This would be encapsulated within the ENIP data
  Data field
    Not always used
    Sometimes only contains a few bytes
    Sometimes contains a large amount of information

## Slide 11: PLC – PROTOCOL RESOURCES
DF1 Protocol and Command Set
Communicating with RA Products using EtherNet/IP Explicit Messaging
EtherNet/IP Adaptation of CIP Specification
Notes: Time: 30sec
Notes:
  Names of three documents that are helpful in understanding the protocol

## Slide 12: PLC – DEVICE CONFIGURATION
Device Model
MicroLogix 1400
Series B
CPU State
REMOTE RUN
SNMP State
DISABLED
Memory Module
Installed
w/o
Write-Protect
Firmware Version
21.003 or below
Notes: Time: 1 minutes
Notes:
  Device Model
    May work on Series A controllers. Did not have one to test on
    Series C may give issues due to the firmware signing
  CPU state
    Most of the attack can be performed in RUN mode
    One part requires REMOTE, forcing this attack to require REMOTE
  SNMP state
    Default state of Disabled
  Memory Module
    Installed (non-default)
    Write-Protect not enforced
  Firmware Version
    21.003 or lower
    Newest before our disclosure

## Slide 13: ENABLING SNMP
Notes: EST Time Marker: 8:45 minutes
Time: 30s
Notes:
  Transition
  Discuss how this is the start of the attack path

## Slide 14: ENABLING SNMP – REASONS & REQUIREMENTS
Reasons
Requirements
Flash New firmware
No Keyswitch Requirement
Firmware Version 21.003 or Below
SNMP Disabled By Default
ENIP Enabled
Notes: Time: 1 minute
Notes:
  Reason
    SNMP is a required element of the firmware flashing process
    SNMP is disabled by default since firmware version 21.0
    Before we can upload our custom firmware we have to find a way to enable the service
  Requirements
    No keyswitch requirement
      This means it can be conducted in any mode including RUN
      This cannot be done in this method through RSLogix
      Emphasize that this is only a queued for enablation
    Firmware version 21.003 or below
      Version 21.004 fixed this when in RUN mode

## Slide 15: ENABLING SNMP - RSLOGIX
Enable SNMP
Reboot Device
Notes: Time: 3 minute
Notes:
  Initial Approach
  RSLogix
    Programming and control software for the MicroLogix line (among others)
  Enable SNMP via the device’s programming software – RSLogix
  Watch the traffic in Wireshark and pick out the related traffic
    Switch the CPU to PROG for a start marker
    Enable the service
    Switch the CPU to RUN for an end marker
  Investigate errors
    TNS issue
    CRC issue when modifications are made
  Mention Dissector

## Slide 16: ENABLING SNMP - RSLOGIX
Notes: Time: 1 minute
- discuss dissector

## Slide 17: ENABLING SNMP – GET CURRENT CONFIG
PCCC Read # 1
File Type: 0x49
Element Number: 0x00
Byte Size: 0x50
File Number: 0x01
Sub-Element Number: 0x00
PCCC Read # 2
Byte Size: 0x50
File Number: 0x01
File Type: 0x49
Element Number: 0x00
Sub-Element Number: 0x28
PCCC Protected Typed Logical Read with Three Address Fields
CMD
Byte Size
FNC
TNS
File Number
File Type
Element Number
Sub-Element Number
Notes: Time: 3minute
Notes:
  To make any changes we need to first know what the existing data is
  Can obtain this via two PCCC Protected Typed Logical Read with Three Address Fields commands
    File Number 0x01
    File Type 0x49
  Structure is a normal PCCC command with the following elements in the data field
    Byte Size
      Number of bytes to read
    File Number
      Specific file to read
    File Type
      Type of that file
      Seems to be more defining than the File Number
    Element Number
      Offset within the file
    Sub-Element Number
      Offset within the file
  Reads are limited to 0x50 bytes, but we need more than 0x50 bytes for the full configuration

## Slide 18: ENABLING SNMP – GET CURRENT CONFIG
Notes: Time: 1minute
Notes:
  Response data of the requested size when the request is successful
  Response 1
    Contains, among other things, the network configuration data
    Ex: four first highlighted bytes indicate the device’s IP address
  Response 2:
    First highlighted byte
      Protocol control byte
      Contains a bitfield of the service states
    Second highlighted bytes:
      CRC for the channel configuration file

## Slide 19: ENABLING SNMP – PROTOCOL BITFIELD
Bit 7 | Bit 6 | Bit 5 | Bit 4 | Bit 3 | Bit 2 | Bit 1 | Bit 0
ENIP | ? | ModbusTCP | DNP3 | ? | SMTP | SNMP | HTTP
PCCC Read # 2 Response - Modified |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00
00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00
00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 02
00 | 00 | 00 | 00 | 0F | 00 | 00 | 52 | 09 | 00 | 7A | 00 | 04 | 00 | 00 | 00
00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00
PCCC Read # 2 Response - Original |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00
00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00
00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00
00 | 00 | 00 | 00 | 0F | 00 | 00 | 52 | 09 | 00 | 7A | 00 | 04 | 00 | 00 | 00
00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00
Notes: Time: 1minute
Notes:
  Protocol Bitfield breaks out as shown above
  Field we’re interested in is SNMP
  Requires that bit 1 is set, giving us the value 0x02 when all other services are toggled off

## Slide 20: ENABLING SNMP – CRC ERRORS

## Slide 21: ENABLING SNMP – REBUILD CONFIG
PCCC Read # 1 Response |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
04 | 00 | 12 | 00 | 00 | 00 | 3C | 00 | 01 | 00 | 03 | 00 | 00 | 00 | 00 | 00
00 | 00 | FF | FF | 00 | 00 | EB | 72 | 05 | 00 | 6A | 00 | 00 | 00 | 84 | 00
98 | 3A | B8 | 0B | 1E | 00 | 00 | 0A | 02 | 00 | FF | FF | 00 | FF | 00 | 0A
01 | 00 | 00 | 00 | 00 | 00 | 00 | 0A | 01 | 00 | 00 | 00 | 00 | 00 | 00 | 00
00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00
PCCC Read # 2 Response - Modified |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00
00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00
00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 02
00 | 00 | 00 | 00 | 0F | 00 | 23 | 92 | 09 | 00 | 7A | 00 | 04 | 00 | 00 | 00
00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00
Notes: Time: 1minute
Notes:
  With the protocol control byte changed, the CRC needs to be updated
  CRC details
    CRC-16
    Calculated across bytes 0x00-0x85
    Placed into bytes 0x86-0x87
  Gotchas with the CRC
    If the byte 0x10 is encountered in the response it will always be repeated
    This is due to compatibility restraints with the serial DF1 protocol where 0x10 is used as an escape
    The repeated 0x10 is necessary when sending data, but it is NOT included when calculating the CRC

## Slide 22: ENABLING SNMP – REBUILD CONFIG
PCCC Write # 1
File Type: 0x49
Element Number: 0x00
Byte Size: 0x50
File Number: 0x01
Sub-Element Number: 0x00
PCCC Write # 2
Byte Size: 0x50
File Number: 0x01
File Type: 0x49
Element Number: 0x00
Sub-Element Number: 0x28
Config Data
Config Data
PCCC Protected Typed Logical Write with Three Address Fields
CMD
Byte Size
FNC
TNS
File Number
File Type
Element Number
Config Data
Sub-Element Number
Notes: Time: 1minute
Notes:
  With the new data we can overwrite the existing configuration
  Can send this via two PCCC Protected Typed Logical Write with Three Address Fields commands
    File Number 0x01
    File Type 0x49
  Structure is almost the same as the Read used earlier, with an added Data field
    Byte Size
      Number of bytes to read
    File Number
      Specific file to read
    File Type
      Type of that file
      Seems to be more defining than the File Number
    Element Number
      Offset within the file
    Sub-Element Number
      Offset within the file
    Data
      The modified data split into two messages
  Writes are limited to 0x50 bytes, but we need more than 0x50 bytes for the full configuration

## Slide 23: ENABLING SNMP – WRITE CONFIG

## Slide 24: ENABLING SNMP – SUCCESS INDICATOR
Advanced Settings
ENET Config
Protocol Setup
ESC
Notes: Time: 1minute
Notes:
  Verification
  Can check on the PLC screen itself
  Navigate using the keypad throught the following menus
    Physical ESC key
    ‘Advanced Set’ menu
    ‘ENET config’ menu
    ‘Protocol Setup’ menu
  Notice that ‘SNMP’ now has the ‘Enabled’ message flashing
  Also will contain the ‘Power Cycle***’ message at the bottom
    This indicates that the change was made to the channel configuration file
    But a reboot is necessary before the service actually gets enabled

## Slide 25: REBOOTING THE PLC
Notes: Est Time Marker: 16 minutes
Time: 10s
Notes:
  Quickly transition

## Slide 26: REBOOTING THE PLC - REASONS & REQUIREMENTS
Reasons
Requirements
Required to Fully Enable SNMP
No Keyswitch Requirement
Firmware Version 21.003 or below
No User Accessible Reboot Functionality
ENIP Enabled
Notes: Time: 1 minutes
Notes:
  Reasons
    As shown earlier
    Need to reboot to make the device fully enable the service
    No documented reboot functionality to leverage
  Requirements
    Using the method we found
    No requirement on keyswitch mode
    This means the device can be in RUN mode
    Requires firmware version 21.003 or below
      The newest during our research
    EtherNet/IP enabled
      Default configuration

## Slide 27: REBOOTING THE PLC – BASIC FUZZING
Notes: ******* need a segway slide
Time: 3 minutes
Notes:
  Attempt some Basic fuzzing
    Piping /dev/urandom directly to the device on port 44818
  Surprisingly works after a while
  Couldn’t consistently reproduce
    Crash still occurred
    Sometimes it took a couple seconds
    Sometimes it took over an hour
  Got lucky and had wireshark running one of the times it crashed in a couple seconds
  Replayed the capture and was able to reproduce every time
  after discovery, cropped the packet to find the affecting bytes
  replaced all irrelevant bytes with nulls for easier reading

## Slide 28: REBOOTING THE PLC – E8FF CRASH
TCP Data |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
00 | 00 | E8 | FF | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00
00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 |  |  |  |  |  |  |  | 
Notes: Time: 2 minutes
Notes:
  Simple case shown above
    Any two bytes to start the packet
    The bytes ‘0xE8 0xFF’
    Any 20 bytes to finish the packet
  Emphasis on the third and fourth byte – highlighted in orange
  I’ll refer to this crash as the E8FF crash throughout the rest of the talk as its is the most consistent part of the crash

## Slide 29: REBOOTING THE PLC – E8FF CRASH
TCP Data |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00
00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00
00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00
00 | 00 | E8 | FF | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00
00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 |  |  |  |  |  |  |  | 
Notes: Time: 1 minutes
Notes:
  Complex case shown above
    Any amount of 24-byte blocks of null characters
    Followed by
    The simple case
  During testing we discovered additional cases that also cause the crash
    Any amount of 24 null byte character groups before the crash block will also cause the crash
    When doing this the preceding bytes MUST be null

## Slide 30: REBOOTING THE PLC – E8FF CRASH
SNMP Change Queued
E8FF Crash
SNMP Back To Default
Notes: Time: 1 minute
Notes:
  Crash successfully triggers a reboot
  Crash also takes away the changes we made to the Channel Configuration File
  Unsure why

## Slide 31: REBOOTING THE PLC – E8FF CRASH
MicroLogix 1400 Programmable Controllers Instruction Set Reference Manual - Appendix C
Notes: Time: 1 minute
Notes:
  Did some looking into the type of fault that is caused when this crash is triggered
  Causes a fault with Error Code 0x02 – Unexpected Reset
  This loads the default program
  Default program
    Not something that we have access to change during any normal operation
    May be able to change it with malicious firmware, but not tested
    Contains a blank project file with default configuration

## Slide 32: REBOOTING THE PLC – E8FF CRASH
MicroLogix 1400 Programmable Controllers Instruction Set Reference Manual - Appendix C
Notes: Time: 1 minute
Notes:
  Did some looking into the type of fault that is caused when this crash is triggered
  Causes a fault with Error Code 0x02 – Unexpected Reset
  This loads the default program
  Default program
    Not something that we have access to change during any normal operation
    May be able to change it with malicious firmware, but not tested
    Contains a blank project file with default configuration

## Slide 33: REBOOTING THE PLC – CRASH RECOVERY
MicroLogix 1400 Programmable Controllers Instruction Set Reference Manual - Appendix B
Notes: Time: 1 minute
Notes:
  Did some looking into ways to modify the default program
  Found a way to load a stored program instead
  By setting the bit S:1/10, the PLC is instructed to load its program from a memory module instead of from the default program
  This allows us to control the post-crash program as long as we can control the memory module program

## Slide 34: MEMORY MODULE
Notes: Est Time Marker: 23:30 minutes
10s
Briefly introduce the section

## Slide 35: MEMORY MODULE - REASONS & REQUIREMENTS
Reasons
Requirements
Storage Persistent Through Crash
Keyswitch in REMOTE mode
Memory Module w/o Write-Protect
Location That Can Restore Program
ENIP Enabled
Programming Routine
Notes: Time: 1 minutes
Notes:
  Reasons
    Need to store our changes in a way that will persist across a device crash
    Need that location to be somewhere that can restore after the crash
  Requirements
    This command requires that the PLC be in the REMOTE keyswitch mode
    Programming mode
      Talked about shortly
    A memory module must be installed in the PLC
      It must not be in Write-Protect mode
    EtherNet/IP enabled
      Default configuration

## Slide 36: MEMORY MODULE – LOAD ON ERROR
Load from Memory Module on Error
Byte Size: 0x02
File Number: 0x02
File Type: 0x84
Element Number: 0x00
Sub-Element Number: 0x01
Config Data: 0x0004
Function Code: 0xAA
PCCC Protected Typed Logical Write with Three Address Fields
CMD
Byte Size
FNC
TNS
File Number
File Type
Element Number
Config Data
Sub-Element Number
Notes: Time: 1 minute
Notes:
  Triggered by a write to the Status file
    File Number 0x02
    File Type 0x84
  forces the PLC to use the memory module program instead of the default
  Requires the programming routine
    By proxy requires REMOTE

## Slide 37: MEMORY MODULE – WRITE NEW CONFIG
Programming Routine
Get Edit Resource
Custom Configuration
Set CPU – REMOTE PROG
Execute Command List
Download Completed
Apply Port Configuration
Return Edit Resource
Notes: Time: 1 minute
Notes:
  Some commands require elevated privileges to execute
  This includes most commands that write configuration information
    Enabling SNMP in the Channel Configuration interestingly does not fall into this category
  To go through this routine, the PLC must be in a programming mode
    PROG would work, but the chances of that are minimal
    Using REMOTE in this example
  Setup Commands
    Change the CPU into a programming state like REMOTE PROG
    Run the ‘Execute Command List’ command
    Run the ‘Get Edit Resource Command’
  Custom Commands
    If the three commands above were successful
    Can send as many commands as necessary
    Any commands can be sent here – not only ones that require escalated privleges
  Confirm Commands
    Run the ‘Download Completed’ command
    Run the ‘Apply Port Configuration’ command
    Run the ‘Return Edit Resource’ command

## Slide 38: MEMORY MODULE – CONFIG VERIFICATION
Notes: Time: 1 minute
Notes:
  If everything was successful
  Can check the PLC’s Status file via RSLogix
  Verify that the ‘Load Memory Module on Memory Error’ bit is set to 1

## Slide 39: MEMORY MODULE – STORE PROGRAM
Store to Memory Module
Data: 0x01000000
Function Code: 0x58
PCCC
CMD
Data
FNC
TNS
Notes: Time: 1 minute
Notes:
  Once the program has been successfully updated
  Issue the command to store the existing program to the PLC’s memory module

## Slide 40: ATTACK SO FAR
Notes: EST Time: 27 min
Briefly introduce the section

## Slide 41: ATTACK SO FAR
Patched Device
Modify Channel Configuration File
Enable Load from Memory Module on Error
Store to Memory Module
Crash the device
Patched Device with SNMP Fully Enabled
Notes: Time: 1 minute
Notes:
  Recap
    Started with a patched device
    Modified the channel configuration file to partially enable SNMP
    Set the program to allow loading from a memory module when an error is encountered
    Stored the new program to a memory module
    Crashed the device with a bad packet
    Waited for the device to reboot
    Ended with a device that has SNMP fully enabled

## Slide 42: MODIFIED FIRMWARE
Notes: EST Time: 28
10s
Briefly introduce the section

## Slide 43: MODIFIED FIRMWARE - CREATION
Notes: ******** ADDRESS THE TECHNICAL STEP BACK
Time: 4 minutes
Notes:
  With SNMP fully enabled, we now have full ability to upload new firmware
  Need to build custom firmware
  Using Patrick DeSantis’ method for firmware creation from his DEFCON25 talk
  series B only implements a checksum for error checking
    can make any changes as long as the net change is zero
    display images of the result when REMOTE is changed to HACKED

## Slide 44: FLASHING FIRMWARE
Notes: EST Time: 29
Briefly introduce the section

## Slide 45: FLASHING FIRMWARE - SNMP BACKDOOR
root@kali:~# snmpwalk -c private -v 1 <ip_addr> .1.3.6.1.4.1.95
iso.3.6.1.4.1.95.2.2.1.1.1.0 = IpAddress: 0.0.0.0
iso.3.6.1.4.1.95.2.2.1.1.2.0 = ""
iso.3.6.1.4.1.95.2.2.1.1.3.0 = Hex-STRING: 00 00 00 00 00 00 00 00 00 00 00 00 00 00
iso.3.6.1.4.1.95.2.2.1.1.4.0 = Hex-STRING: 00 00 00 00 00 00 00 00
iso.3.6.1.4.1.95.2.2.1.1.5.0 = Hex-STRING: 00 00 00 00 00 00
iso.3.6.1.4.1.95.2.2.1.1.6.0 = INTEGER: 0
iso.3.6.1.4.1.95.2.2.1.1.7.0 = INTEGER: 0
iso.3.6.1.4.1.95.2.2.2.3.0 = INTEGER: 4
iso.3.6.1.4.1.95.2.3.1.1.1.1.0 = INTEGER: 1
iso.3.6.1.4.1.95.2.3.1.1.1.2.0 = INTEGER: 1
iso.3.6.1.4.1.95.2.3.1.1.1.3.0 = STRING: "public"
iso.3.6.1.4.1.95.2.3.1.1.1.4.0 = IpAddress: 0.0.0.0
iso.3.6.1.4.1.95.2.4.1.0 = STRING: "wheel"
iso.3.6.1.4.1.95.2.4.2.0 = STRING: "public"
iso.3.6.1.4.1.95.2.4.3.0 = STRING: "private"
End of MIB
root@kali:~#
Notes: Time: 1 minutes
Notes:
  Flashing firmware is conducted in three phases
    Setup
    Transfer
    Flashing
  The setup phase requires sending three SNMP write commands
    1) Set the IP Address of the TFTP server
    2) Set the name of the firmware file on the TFTP server
    3) Reboot the device
      NOTE: this is the same reboot we talked about earlier
  All of these commands require use of a privileged SNMP Community string
    Here we can leverage a backdoor string discovered by Patrick DeSantis in 2016
    Still not patched

## Slide 46: FLASHING FIRMWARE – SNMP REBOOT
root@kali:~# snmpset -c wheel -v 1 <ip_addr> .1.3.6.1.4.1.95.2.3.1.1.1.1.0 i 2
Notes: Time: 2 minutes
Notes:
  First method for a reboot that we discovered
  When a device is going through a firmware update we noticed that the device reboots
  Investigated what traffic is sent when a firmware update is requested
  Will discuss the entire process later
  One message was of particular interest
    A write to the OID shown above
    Value integer 2
  Causes the device to reboot
  If none of the other information for a firmware update is sent the device will reboot without entering the firmware update cycle
  Command above leverages an undocumented privileged community string disclosed by Patrick DeSantis in TALOS-2016-0184

## Slide 47: FLASHING FIRMWARE – SNMP REBOOT
Reboot required to enable SNMP
SNMP required to reboot device
Notes: Time: 1 minute
Notes:
  Did not end up working for our purposes as it created a catch 22
  Still useful if SNMP is already enabled and we want to enable a different service
  Requires the device be in PROG or REMOTE mode
    Comment on the contradiction from the slides before
  Required us to keep looking

## Slide 48: FLASHING FIRMWARE - TFTP
Notes: Time: 1 minutes
Notes:
  Once a reboot is triggered, the PLC reaches out to the defined TFTP server requesting the desired file
    TFTP server must be accessible
    File must exist and be readable
  If all conditions are met, the PLC starts downloading the new firmware file
  Once the transfer has completed, integrity checks are calculated

## Slide 49: FLASHING FIRMWARE – UPDATE PROCESS
Notes: Time: 1 minutes
Notes:
  If the integrity checking passes, the device will move on to the flashing stage
  This can be verified by the screen shown here displaying on the PLC
  If the operation succeeds, the PLC will reboot once more

## Slide 50: FLASHING FIRMWARE – SUCCESS
Notes: Time: 1 minutes
Notes:
  When the PLC comes back up, the new firmware will be running
  Shown in the example above with the label ‘HACKED’ in place of the previous ‘REMOTE’

## Slide 51: DEMO
Notes: EST Time: 31

## Slide 53: IMPACT
Notes: EST Time: 33 minutes
10s
Briefly introduce the section

## Slide 54: IMPACT
Important to remember the modification was made at the firmware level
Consequential changes are possible via this strategy with enough time/money
“… you can’t really tell if the logic running on the controller is what you uploaded …” – R. Wightman about TRISIS @ S4x18
Notes: Time: 8 minutes
Notes:
  No secret that just changing the text for a state doesn’t affect the operation of the device
  We need to understand the broader implications of how that change was made
    Any piece of the firmware could have been changed
    Ranging from
      other minor display changes
      Modified code executed before runtime
  with enough time and money this strategy could be used for consequential changes
  Taking it a step further
    if the checksum is determined our strategy wouldn't be necessary anymore
  Reid Wightman made a comment at S4x18
    … you can’t really tell if the logic running on the controller is what you uploaded …”
    He was talking about the TRISIS situation, but the comment stuck with me
  Since we control the firmware completely we are capable of making it do whatever we want
    Including lie to its operators
  After all it’s a computer at the end of the day

## Slide 55: MITIGATION
Notes: EST Time: 34:30
10s
So, how do we fix it

## Slide 56: MITIGATION – RECOMMENDATIONS
Keyswitch RUN mode
Firmware Version >= 21.004
Follow proper network segmentation practices
Monitor your network for suspicious activity
Notes: Time: 1 minute
Notes:
  Standard recommendations
    Make sure your device is left in the RUN keyswitch mode at all times when not being programmed
    Follow proper network segmentation practices
    Monitor network for suspicious activity
    Apply firmware version 21.004 or newer to your MicroLogix 1400

## Slide 57: MITIGATION – SPECIAL RECOMMENDATIONS
Enable Write-Protect on memory modules
Enable Snort Rules 44419 through 44429
Successful in Keyswitch RUN
Enable SNMP Setting (CVE-2017-14462)
E8FF Crash (CVE-2017-12088)
Device Fault (CVE-2017-14470)
Read Ladder Logic (CVE-2017-14472)
Read Master Password (CVE-2017-14473)
Notes: Time: 2 minutes
Notes:
  Special Recommendations
    Enable Write-Protect on any memory module in use
      This will prevent any future writes
      Make sure the program is correct, however, as only 1 write is possible
    Enable SNORT sids above
      These will detect and alert on additional vulnerabilities discovered that do not require the keyswitch to be in REMOTE

## Slide 58: RESOURCES
Notes: EST Time: 36

## Slide 59: ADDITIONAL RESOURCES
Wireshark Dissector
github.com/wireshark/wireshark/blob/master/epan/dissectors/packet-cip.h
White Paper
talosintelligence.com/resources/62
Relevant Blog Posts
blog.talosintelligence.com/2018/03/ab-micrologix-1400-multiple-vulns.html
blog.talosintelligence.com/2016/08/rockwell-snmp-vuln.html
Talos IDs
TALOS-2017-0440
- through -
TALOS-2017-0445
Snort Coverage
SID 44419
- through -
SID 44429
Contact
jared.rittle@cisco.com
@talossecurity
blog.talosintelligence.com
Notes: End time : 37